{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["AC-Heat Pump","AC-Furnace"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"AC-Heat Pump","index":0,"n_rows":136,"n_cols":34,"rows_kept":136,"cut":false,"hidden":false,"merged":[[0,0,1,31],[44,0,44,31],[132,0,132,31],[89,0,89,31],[110,1,111,5],[112,1,114,5]],"flags":["formulas_cached_only"]}
["ENERGY STAR in Cooperation with ABC Electric Company\nInstallation Commissioning Report for Central AC and Heat Pump",{"$nulls":32},"OMB Control No. 2060-0586"]
[]
[]
[null,"Site Information"]
[null,"Customer name (name on electric bill):"]
[null,"Customer electric utility account number:"]
[null,"Address: "]
[null,"City: ",{"$nulls":15},"State: ",{"$nulls":6},"Zip: "]
[]
[null,"Design"]
[null,"Type of installation:",{"$nulls":5},"q","Replacement",{"$nulls":4},"q","New system - existing home",{"$nulls":8},"q","New system - new home"]
[{"$nulls":7},"q","AC only",{"$nulls":4},"q","Heat only",{"$nulls":8},"q","AC & heat"]
[null,"Area of zone served by unit:",{"$nulls":14},"sq ft",null,null,null,"# of units in home:"]
[null,"Is the unit self-contained, or is fan/airflow provided by external device (furnace)?"]
[null,"Heat gain method: ",{"$nulls":5},"q","Manual J v7",null,null,null,"q","Manual J v8",null,null,null,"q","None",null,null,"q","Other:"]
[null,"Duct design method:",{"$nulls":5},"q","Manual D",null,null,null,"q","None",null,null,null,"q","Other:"]
[null,"Equipment specification method: ",{"$nulls":9},"q","Manual S",null,null,null,"q","OEM recommendation",{"$nulls":6},"q","Other:"]
[null,"Latent heat gain: ",{"$nulls":12},"BTUh",null,null,null,"Sensible heat gain: ",{"$nulls":10},"BTUh"]
[null,"Total heat gain: ",{"$nulls":12},"BTUh",null,null,null,"Design airflow:",{"$nulls":10},"CFM"]
[null,"Duct design static pressure:",{"$nulls":12},"IWC",null,null,null,"Design heat loss:",{"$nulls":10},"BTUh"]
[]
[null,"Equipment"]
[null,"Condenser",null,null,null,"Manufacturer:",{"$nulls":15},"Model: "]
[{"$nulls":5},"Serial number: "]
[null,"Evaporator",null,null,null,"Manufacturer:",{"$nulls":15},"Model: "]
[{"$nulls":5},"Serial number: "]
[null,"System",null,null,null,"Metering device:",{"$nulls":4},"q","TXV",null,null,"q","Fixed orifice",null,null,null,"q","Other:"]
[{"$nulls":5},"Refrigerant:",{"$nulls":4},"q","R-22",null,null,"q","R-410a",null,null,null,"q","Other:"]
[null,"Fan Motor Type:",{"$nulls":4},"q","Fixed speed (e.g. PSC)",{"$nulls":6},"q","Variable (e.g. ECM/ICM)",{"$nulls":6},"q","Other:"]
[null,"Cooling",null,null,null,"Latent Capacity: ",{"$nulls":9},"BTUh",null,null,null,"ARI EER/SEER: "]
[{"$nulls":5},"Sensible Capacity: ",{"$nulls":9},"BTUh",null,null,null,"ARI Ref #:"]
[{"$nulls":5},"Total Capacity: ",{"$nulls":9},"BTUh"]
[null,"Heating",null,null,null,"HSPF:"]
[{"$nulls":5},"At 17oF",null,null,null,"Capacity: ",{"$nulls":8},"BTUh",null,null,null,"COP:"]
[{"$nulls":5},"At 47oF",null,null,null,"Capacity: ",{"$nulls":8},"BTUh",null,null,null,"COP:"]
[null,"Previous equipment - for replacements only"]
[null,null,"Cooling",{"$nulls":4},"Total capacity:",{"$nulls":7},"Btuh",null,null,null,"ARI EER/SEER: "]
[null,null,"Heating",{"$nulls":4},"HSPF:"]
[{"$nulls":7},"At 17oF",null,null,null,"Capacity: ",{"$nulls":8},"BTUh",null,null,null,"COP:"]
[{"$nulls":7},"At 47oF",null,null,null,"Capacity: ",{"$nulls":8},"BTUh",null,null,null,"COP:"]
[]
[]
[]
[]
["AC & Heat Pump Installation Commissioning Report (Page 2 of 3)"]
[null,"Equipment - continued"]
[]
[null,"Does capacity meet requirement of 95-115% (or up to 125% for heat pumps with heat dominated requirements)"]
[null,"of calculated load or the next nominal size?",{"$nulls":12},"q","Yes",null,"q","No"]
[]
[null,"Refrigerant Tests - run system for 15 minutes before testing"]
[null,"Date:",{"$nulls":12},"Outdoor ambient temp. (at condenser):",{"$nulls":14},"oF DB"]
[null,"Time of test:",{"$nulls":12},"Outdoor relative humidity - optional:"]
[{"$nulls":14},"Barometric pressure - optional:"]
[null,"Air temperatures measured in duct near evaporator (not in conditioned building space):"]
[{"$nulls":4},"Cooling Mode",{"$nulls":4},"Return",{"$nulls":7},"oF DB",{"$nulls":7},"oF WB"]
[{"$nulls":9},"Supply",{"$nulls":7},"oF DB",{"$nulls":7},"oF WB"]
[{"$nulls":4},"Heating Mode",{"$nulls":4},"Return",{"$nulls":7},"oF DB"]
[{"$nulls":9},"Supply",{"$nulls":7},"oF DB"]
[null,"Liquid line pressure: ",{"$nulls":10},"psi",{"$nulls":4},"Liquid line temp.: ",{"$nulls":10},"oF DB"]
[null,"Suction line pressure: ",{"$nulls":10},"psi",{"$nulls":4},"Suction line temp.: ",{"$nulls":10},"oF DB"]
[null,"Refrigerant Calculations",{"$nulls":7},"Condenser sat. temp. (from liquid pressure):",{"$nulls":15},"oF DB"]
[{"$nulls":9},"Evaporator sat. temp. (from suction pressure):",{"$nulls":15},"oF DB"]
[null,"Subcooling (condensing temp. - liquid line temp.):",{"$nulls":16},"oF DB"]
[null,"Superheat (suction line temp. - evaporating temp.):",{"$nulls":16},"oF DB"]
[null,"For TXV"]
[null,null,"OEM subcooling goal:",{"$nulls":9},"oF DB"]
[null,null,"Subcooling deviation (subcooling - subcooling goal):",{"$nulls":16},"oF DB"]
[null,"For Fixed Orifice"]
[null,null,"Superheat goal (from superheat lookup tables, based on outdoor ambient and return air wet bulb temps.):",{"$nulls":26},"oF DB"]
[null,null,"Superheat deviation (superheat goal - superheat):",{"$nulls":16},"oF DB"]
[]
[null,"Does system meet requirement of subcooling within ±3oF or superheat within ±5oF of goal?",{"$nulls":24},"q","Yes",null,"q","No"]
[]
[null,"Electrical Measurements - taken at time of refrigerant tests"]
[null,"Evaporator/air handler fan:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[null,"Condenser fan:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[null,"Compressor:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[]
[null,"Electrical Requirements"]
[null,"Does system meets requirements of ACCA QI 4.3? ",{"$nulls":14},"q","Yes",null,"q","No"]
[]
[null,"Air Flow Tests"]
[null,"Date:",{"$nulls":12},"Outdoor ambient temp. (at condenser):",{"$nulls":14},"oF DB"]
[null,"Time of test:",{"$nulls":12},"Outdoor relative humidity - optional:"]
[{"$nulls":14},"Barometric pressure - optional:"]
[null,"Measured air volume at evaporator: ",{"$nulls":13},"CFM"]
[]
[]
["AC & Heat Pump Installation Commissioning Report (Page 3 of 3)"]
[null,"Air Flow Tests - continued"]
[null,"Test peformed in heating or cooling mode?",{"$nulls":12},"q","Heating",null,null,"q","Cooling"]
[null,"Static pressure",{"$nulls":4},"Return",null,null,"Static:",{"$nulls":5},"IWC",null,"   Measurement location:"]
[{"$nulls":6},"Supply",null,null,"Static:",{"$nulls":5},"IWC",null,"   Measurement location:"]
[null,"Measurement method used:",{"$nulls":7},"q","TrueFlow",null,null,"q","Pressure matching (with Duct Blaster)",{"$nulls":9},"q","Anemometer"]
[{"$nulls":9},"q","Fan Curve",null,null,"q","Temperature split (heating only)",{"$nulls":9},"q","Other:"]
[null,"Speed Setting",{"$nulls":4},"If fixed",null,"qLow qMed-Low qMed qMed-High qHigh",{"$nulls":15},"  CFM (at 0.5 IWC):"]
[{"$nulls":6},"If variable",null,null,null,"Fan set for",{"$nulls":6},"CFM/ton"]
[]
[null,"Does air flow meet requirement of 350-450 cfm or within range recommended by OEM?",{"$nulls":24},"q","Yes",null,"q","No"]
[]
[null,"Duct Leakage"]
[null,"Initial Test",{"$nulls":4},"Date:",{"$nulls":10},"Time:"]
[null,"Final Test",{"$nulls":4},"Date:",{"$nulls":10},"Time:"]
[null,"Test method used:",{"$nulls":5},"q","Duct Blaster",null,null,null,"q","Blower Door Subtraction",{"$nulls":7},"q","Other:"]
[null,"Existing system duct leakage:",{"$nulls":11},"CFM"]
[null,"Post Installation duct leakage:",{"$nulls":11},"CFM",null,null,null,"Leakage % reduction ([existing-post]/existing):"]
[null,"Total % leakage (post leakage/design flow):",{"$nulls":13},"OR  (post leakage/measured flow):"]
[]
[null,"Does duct leakage meet one of the following requirements:"]
[null,"existing\nhomes:",{"$nulls":4},"q","  No more than 20% of total air flow"]
[{"$nulls":6},"q","  A reduction of 50% or more from the initial measurement"]
[null,"new construction:",{"$nulls":4},"q","  Leakage from ducts inside the thermal envelope is no more than 10% of total air flow"]
[{"$nulls":6},"q","  No more than 6% of total air flow from ducts outside the thermal envelope"]
[{"$nulls":6},"q","  Less than 4 CFM leakage to outdoors per 100 square feet of conditioned floor area"]
[]
[null,"System Controls"]
[null,"Does system meets requirements of ACCA QI 4.6? ",{"$nulls":14},"q","Yes",null,"q","No"]
[]
[null,"System Documentation & Owner Education"]
[null,"Copies of this report and OEM manuals left with owner?",{"$nulls":15},"q","Yes",null,"q","No"]
[null,"Demonstrated system for owner? ",{"$nulls":9},"q","Yes",null,"q","No"]
[]
[null,"Contractor/Technician Information"]
[null,"Technician name:"]
[null,"Company:"]
[null,"Address 1: "]
[null,"Address 2: "]
[null,"City: ",{"$nulls":16},"State: ",{"$nulls":6},"Zip: "]
[null,"Phone/Email: "]
[null,"Technician signature: "]
[]
["Please send completed forms to: System Implementer, 123 Main St, Town, ST, 01234, FAX 555-123-4567"]
["EPA Form 5900-180"]
["The government estimates the average time needed to fill out this form is 2 hours and welcomes suggestions for reducing this effort. "]
["Send comments (referencing OMB Control Number) to the Director, Collection Strategies Division, U.S. EPA (2822T), 1200 Pennsylvania Ave., NW, Washington, D.C. 20460."]

{"sheet":"AC-Furnace","index":1,"n_rows":172,"n_cols":31,"rows_kept":172,"cut":false,"hidden":false,"merged":[[0,0,1,31],[46,0,46,31],[171,0,171,31],[91,0,91,31],[138,0,138,31],[122,1,123,5],[124,1,126,5]],"flags":["formulas_cached_only"]}
["ENERGY STAR in Cooperation with ABC Electric Company\nInstallation Commissioning Report for Central AC and Furnace"]
[]
[]
[null,"Site Information"]
[null,"Customer name (name on electric bill):"]
[null,"Customer electric utility account number:"]
[null,"Address: "]
[null,"City: ",{"$nulls":15},"State: ",{"$nulls":6},"Zip: "]
[]
[null,"Design"]
[null,"Type of installation:",{"$nulls":5},"q","Replacement",{"$nulls":4},"q","New system - existing home",{"$nulls":8},"q","New system - new home"]
[{"$nulls":7},"q","AC only",{"$nulls":4},"q","Heat only",{"$nulls":8},"q","AC & heat"]
[null,"Area of zone served by unit:",{"$nulls":14},"sq ft",null,null,null,"# of units in home:"]
[null,"Heat gain method: ",{"$nulls":5},"q","Manual J v7",null,null,null,"q","Manual J v8",null,null,null,"q","None",null,null,"q","Other:"]
[null,"Duct design method:",{"$nulls":5},"q","Manual D",null,null,null,"q","None",null,null,null,"q","Other:"]
[null,"Equipment specification method: ",{"$nulls":9},"q","Manual S",null,null,null,"q","OEM recommendation",{"$nulls":6},"q","Other:"]
[null,"Latent Heat Gain: ",{"$nulls":12},"BTUh",null,null,null,"Sensible Heat Gain: ",{"$nulls":10},"BTUh"]
[null,"Total Heat Gain: ",{"$nulls":12},"BTUh",null,null,null,"Design Airflow:",{"$nulls":10},"CFM"]
[null,"Duct Design Static Pressure:",{"$nulls":12},"IWC",null,null,null,"Design heat loss:",{"$nulls":10},"BTUh"]
[]
[null,"Equipment - AC"]
[null,"Condenser",null,null,null,"Manufacturer:",{"$nulls":15},"Model: "]
[{"$nulls":5},"Serial number: "]
[null,"Evaporator",null,null,null,"Manufacturer:",{"$nulls":15},"Model: "]
[{"$nulls":5},"Serial number: "]
[null,"System",null,null,null,"Metering device:",{"$nulls":4},"q","TXV",null,null,"q","Fixed orifice",null,null,null,"q","Other:"]
[{"$nulls":5},"Refrigerant:",{"$nulls":4},"q","R-22",null,null,"q","R-410a",null,null,null,"q","Other:"]
[null,"Fan Motor Type:",{"$nulls":4},"q","Fixed speed (e.g. PSC)",{"$nulls":6},"q","Variable (e.g. ECM/ICM)",{"$nulls":6},"q","Other:"]
[null,"Speed setting",{"$nulls":4},"If fixed",null,"qLow qMed-Low qMed qMed-High qHigh",{"$nulls":15},"  CFM (at 0.5 IWC):"]
[{"$nulls":6},"If variable",null,null,null,"Fan set for",{"$nulls":6},"CFM"]
[null,"Latent Capacity: ",{"$nulls":9},"BTUh",{"$nulls":6},"ARI EER/SEER: "]
[null,"Sensible Capacity: ",{"$nulls":9},"BTUh",{"$nulls":6},"ARI Ref #:"]
[null,"Total Capacity: ",{"$nulls":9},"BTUh"]
[null,"Previous equipment - for replacements only"]
[null,null,"Total capacity:",{"$nulls":8},"Btuh",{"$nulls":6},"ARI EER/SEER: "]
[]
[null,"Does capacity meet requirement of 95-115% of calculated load or the next nominal size?",{"$nulls":24},"q","Yes",null,"q","No"]
{"$rows_empty":9}
["AC & Furnace Installation Commissioning Report (Page 2 of 4)"]
[null,"Equipment - Furnace"]
[null,"Manufacturer:",{"$nulls":19},"Model: "]
[null,"Serial number: ",{"$nulls":19},"AFUE:"]
[null,"Gross capacity:",{"$nulls":9},"Btuh",null,null,"Net capacity:",{"$nulls":8},"Btuh"]
[]
[null,"Previous equipment - for replacements only"]
[null,null,"Gross capacity:",{"$nulls":8},"Btuh",null,null,"Net capacity:",{"$nulls":8},"Btuh"]
[null,"Fuel type:",null,null,null,"q","Gas",null,"q","Oil",null,"q","Propane",null,null,null,"q","Other:"]
[null,"Sealed combustion?",{"$nulls":5},"q","Yes",null,"q","No"]
[null,"Fan Motor Type:",{"$nulls":4},"q","Fixed speed (e.g. PSC)",{"$nulls":6},"q","Variable (e.g. ECM/ICM)",{"$nulls":6},"q","Other:"]
[null,"Speed Setting",{"$nulls":4},"If fixed",null,"qLow qMed-Low qMed qMed-High qHigh",{"$nulls":15},"  CFM (at 0.5 IWC):"]
[{"$nulls":6},"If variable",null,null,null,"Fan set for",{"$nulls":6},"CFM"]
[]
[null,"Does capacity meet requirement of 100-140% of calculated load or the next nominal size?",{"$nulls":24},"q","Yes",null,"q","No"]
[]
[null,"Refrigerant Tests - run system for 15 minutes before testing"]
[null,"Date:",{"$nulls":12},"Outdoor ambient temp. (at condenser):",{"$nulls":14},"oF DB"]
[null,"Time of test:",{"$nulls":12},"Outdoor relative humidity - optional:"]
[{"$nulls":14},"Barometric pressure - optional:"]
[null,"Air temperatures measured in duct near evaporator (not in conditioned building space):"]
[{"$nulls":4},"Cooling Mode",{"$nulls":4},"Return",{"$nulls":7},"oF DB",{"$nulls":7},"oF WB"]
[{"$nulls":9},"Supply",{"$nulls":7},"oF DB",{"$nulls":7},"oF WB"]
[null,"Liquid line pressure: ",{"$nulls":10},"psi",{"$nulls":4},"Liquid line temp.: ",{"$nulls":10},"oF DB"]
[null,"Suction line pressure: ",{"$nulls":10},"psi",{"$nulls":4},"Suction line temp.: ",{"$nulls":10},"oF DB"]
[null,"Refrigerant Calculations",{"$nulls":7},"Condenser sat. temp. (from liquid pressure):",{"$nulls":15},"oF DB"]
[{"$nulls":9},"Evaporator sat. temp. (from suction pressure):",{"$nulls":15},"oF DB"]
[null,"Subcooling (condensing temp. - liquid line temp.):",{"$nulls":16},"oF DB"]
[null,"Superheat (suction line temp. - evaporating temp.):",{"$nulls":16},"oF DB"]
[null,"For TXV"]
[null,null,"OEM subcooling goal:",{"$nulls":9},"oF DB"]
[null,null,"Subcooling deviation (subcooling - subcooling goal):",{"$nulls":16},"oF DB"]
[null,"For Fixed Orifice"]
[null,null,"Superheat goal (from superheat lookup tables, based on outdoor ambient and return air wet bulb temps.):",{"$nulls":26},"oF DB"]
[null,null,"Superheat deviation (superheat goal - superheat):",{"$nulls":16},"oF DB"]
[]
[null,"Does system meet requirement of subcooling within ±3oF or superheat within ±5oF of goal?",{"$nulls":24},"q","Yes",null,"q","No"]
{"$rows_empty":8}
["AC & Furnace Installation Commissioning Report (Page 3 of 4)"]
[null,"Electrical Measurements - taken at time of refrigerant tests"]
[null,"Evaporator/air handler fan:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[null,"Condenser fan:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[null,"Compressor:",{"$nulls":11},"amps",{"$nulls":6},"volts",{"$nulls":6},"watts"]
[]
[null,"Electrical Requirements"]
[null,"Does system meets requirements of ACCA QI 4.3? ",{"$nulls":14},"q","Yes",null,"q","No"]
[]
[null,"Air Flow Tests"]
[null,"Date:",{"$nulls":12},"Outdoor ambient temp. (at condenser):",{"$nulls":14},"oF DB"]
[null,"Time of test:",{"$nulls":12},"Outdoor relative humidity - optional:"]
[{"$nulls":14},"Barometric pressure - optional:"]
[null,"Measured air volume at evaporator: ",{"$nulls":12},"CFM"]
[null,"Test peformed in heating or cooling mode?",{"$nulls":12},"q","Heating",null,null,"q","Cooling"]
[null,"Static pressure",{"$nulls":4},"Return",null,null,"Static:",{"$nulls":5},"IWC",null,"   Measurement location:"]
[{"$nulls":6},"Supply",null,null,"Static:",{"$nulls":5},"IWC",null,"   Measurement location:"]
[null,"Measurement method used:",{"$nulls":7},"q","TrueFlow",null,null,"q","Pressure matching (with Duct Blaster)",{"$nulls":9},"q","Anemometer"]
[{"$nulls":9},"q","Fan Curve",null,null,"q","Temperature split (heating only)",{"$nulls":9},"q","Other:"]
[]
[null,"Does air flow meet requirement of 350-450 cfm or within range recommended by OEM?",{"$nulls":24},"q","Yes",null,"q","No"]
[]
[null,"Duct Leakage"]
[null,"Initial Test",{"$nulls":4},"Date:",{"$nulls":10},"Time:"]
[null,"Final Test",{"$nulls":4},"Date:",{"$nulls":10},"Time:"]
[null,"Test method used:",{"$nulls":5},"q","Duct Blaster",null,null,null,"q","Blower Door Subtraction",{"$nulls":7},"q","Other:"]
[null,"Existing system duct leakage:",{"$nulls":11},"CFM"]
[null,"Post Installation duct leakage:",{"$nulls":11},"CFM",null,null,null,"Leakage % reduction ([existing-post]/existing):"]
[null,"Total % leakage (post leakage/design flow):",{"$nulls":13},"OR  (post leakage/measured flow):"]
[]
[null,"Does duct leakage meet one of the following requirements:"]
[null,"existing\nhomes:",{"$nulls":4},"q","  No more than 20% of total air flow"]
[{"$nulls":6},"q","  A reduction of 50% or more from the initial measurement"]
[null,"new construction:",{"$nulls":4},"q","  Leakage from ducts inside the thermal envelope is no more than 10% of total air flow"]
[{"$nulls":6},"q","  No more than 6% of total air flow from ducts outside the thermal envelope"]
[{"$nulls":6},"q","  Less than 4 CFM leakage to outdoors per 100 square feet of conditioned floor area"]
{"$rows_empty":11}
["AC & Furnace Installation Commissioning Report (Page 4 of 4)"]
[null,"Gas Combustion Test"]
[null,"Altitude derating factor (from site elevation):"]
[null,"Return air:",{"$nulls":8},"oF DB",{"$nulls":4},"Supply air:",{"$nulls":8},"oF DB"]
[null,"Orifice size:",{"$nulls":13},"Manifold pressure:",{"$nulls":10},"psi"]
[null,"Gas meter test dial size:"]
[null,"Gas meter seconds for one revolution of meter:",{"$nulls":13},"Low:",{"$nulls":8},"High:"]
[null,"Gas combustion test calculations"]
[null,null,"Gas rate (from meter lookup tables):",{"$nulls":9},"Low speed:",{"$nulls":9},"High speed:"]
[null,null,"Actual firing rate:",{"$nulls":9},"Low speed:",{"$nulls":9},"High speed:"]
[{"$nulls":12},"Percent:",{"$nulls":9},"Percent:"]
[null,null,"Temperature rise:",{"$nulls":9},"Low speed:",{"$nulls":7},"oF",null,"High speed:",{"$nulls":7},"oF"]
[]
[null,"Combustion Analyzer - required for oil systems, optional for other fuels"]
[null,"O2:",{"$nulls":8},"Stack temperature:",{"$nulls":10},"oF",null,"Efficiency:"]
[null,"CO:",{"$nulls":8},"Draft pressure:",{"$nulls":9},"psi"]
[]
[null,"System Controls"]
[null,"Does system meets requirements of ACCA QI 4.6? ",{"$nulls":14},"q","Yes",null,"q","No"]
[]
[null,"System Documentation & Owner Education"]
[null,"Copies of this report and OEM manuals left with owner?",{"$nulls":15},"q","Yes",null,"q","No"]
[null,"Demonstrated system for owner? ",{"$nulls":9},"q","Yes",null,"q","No"]
[]
[null,"Contractor/Technician Information"]
[null,"Technician name:"]
[null,"Company:"]
[null,"Address 1: "]
[null,"Address 2: "]
[null,"City: ",{"$nulls":16},"State: ",{"$nulls":6},"Zip: "]
[null,"Phone/Email: "]
[null,"Technician signature: "]
[]
["Please send completed forms to: System Implementer, 123 Main St, Town, ST, 01234, FAX 555-123-4567"]